## Sheet1
CSIR-NORTH EAST INSTITUTE OF SCIENCE & TECHNOLOGY
(Council of scientific and industrial research)
NAME OF WORK : Replacement of defective underground service connection to renovated SA type quarters at CSIR-NEIST, Jorhat
Sl No | Particulars of the item | Qnty | Unit | Rate in figures in Rs. | Rate in words | Amount in Rs.
1 | Supplying and laying of 4 x 70 sq.mm size PVC insulated and sheathed 11 kV grade aluminium strainded armoured underground cable laid in ground/partially in air including excavation of cable trench up to 75cm depth refilling, protecting brick covering , sand cushion etc complete handling surplus soil in proper place and proper size of cable lug, cable arrow mark as specified and directed by department. (Havells/Finolex/Polycab Make) | 170 | Mtr
2 | Supplying and laying of 4 x 35 sq.mm size PVC insulated and sheathed 11 kV grade aluminium strainded armoured underground cable laid in ground/partially in air including excavation of cable trench up to 75cm depth refilling, protecting brick covering , sand cushion etc complete handling surplus soil in proper place and proper size of cable lug, cable arrow mark as specified and directed by department. (Havells/Finolex/Polycab Make) | 300 | Mtr
3 | Supplying incuding installation commissioning of vermin and dust proof tatally enclosed hosphatised powder painted cubical outdoor type double door floor mounted compartmental panel board of size 08Mx0.8Mx0.4M made of 16SWG ticck CI sheet and 35mmx35mmx5mm size angle having 4 nos legs at the bottom and CR sheet roofing on the top. The board is to be erected in 1:3:6 PCC foundation including excavation trench and brick soling etc. complete with all internal wiring and provision for 160A 4Pole MCCB incomer. and confirimin to IP-65. (without Incoming MCCB) | 1 | Each
(i) 40mmx5mm 4 strip copper busbar of length 0.2M each
(ii) Digital voltmeter.Accuraacy calss 0.5-1 No. with selector switch
(ii) Digital Ammeter.Accuraacy calss 0.5-1 No. with selector switch
(iii) Pilot lamp-03 Nos.
(iv) 2A slide fuse unit-3 Nos.
4 | Supplying with fitting and fixing panel mounting open execution 25/35KA 415V 50Hz 4P MCCB (without enclosure) of the following capacity complete with making necessary connection as specified by department
| (i) 25KA 100A 4P MCCB | 4 | Each
| (ii) 35KA 160 4P MCCB | 1 | Each
5 | Supplying with fitting and fixing sheet steel phosphatised powder painted single door surface mounting MCCB enclosure fitted on wall or existing iron frame with nuts & bolts as required complete with all necessary connection as specified by department. Havells/ABB.Legrand / Indoasin Make
| (i) For 100 A 4P MCCB | 4 | Each
6 | Supplying including fittting and fixing of bus bar chamber (HPL/GECO/Sputink Make) with 4 strip bus bar of length 450/600 mm made of alluminium alloy or wrought aluminium suitable for following capacity complete with all accessories including connection etc as required.
| (i) 100 A capacity of length 450mm | 4 | Each
Total tender Cost in Rs.
Rupees :
only