## Sheet1
CSIR-NORTH EAST INSTITUTE OF SCIENCE & TECHNOLOGY
(Council of scientific and industrial research)
NAME OF WORK : Electrical renovation works to Technology Demonstration room at CSIR-NEIST, Jorhat
Sl No | Particulars of the item | Qnty | Unit | Rate in figures in Rs. | Rate in words | Amount in Rs.
1 | Wiring for light/fan /exhaust fan/call bell point with 1.5 sq. mm. Size PVC insulated unsheathed 1.1 KV grade approved by the department single core multistrand copper conductor cable(Finolex/Havells/L&T Make) in surface PVC cashing caping wiring system including 6A single way flash tyep switch (Maru Neo Speed /Indoasian Make) ceiling rose , angle holder (Maru Neo speed/Indoasian , 4x4 PVC switch board (Presto Plast) etc in 19 mm size flate PVC cashing caping (Presto Plast Make) complete as required and directed by deptt. Long Point | 29 | Each
2 | Wiring for 5 pin 16 A power plug point with 4.0 sq. mm PVC insulated unsheathed multistrand (Finolex/Havells/ Make) single core copper conductor cable in surface PVC cashing caping (Presto Plast) wiring system including providing and fixing 5 pin 16 A flush type switch (Maru Neo speed/Anchor Penta /Indoasian) and socket (Maru neo speed, Anchor Penta/Indoasian) , fitted on 8 x 6 size PVC switch board cover including earth continuity with 2.5 sq.mm wire to the third pin of the plug socket etc complete as required and specified by deptt.
| (a) Medium Point up to 6.00 M Length | 6 | Each
| (b) Long point up to 10.00 M Length | 12 | Each
3 | Wiring for sub-main wiring with the following size of PVC insulated, unsheathed wire, single core cable (Finolex/HavellsMake) in surface PVC cashing caping (presto Plast) as required.
| (a) With 2x 2.5 sq. mm. + earth continuity 1x 1.5 sq. mm. PVC insulated unsheathed single core copper in PVC cashing caping. | 50 | Mtr
| (a) With 2x 6.0 sq. mm. + earth continuity 1x 4.0 sq. mm. PVC insulated unsheathed single core copper in PVC cashing caping. | 60 | Mtr
| (b) With 4 x 4 sq. mm. + earth continuity 2 x 2.5 sq. mm. PVC insulated unsheathed single core copper in PVC cashing caping. | 60 | Mtr
| (c ) With 4x 16 sq. mm. + earth continuity 2 x 10 sq. mm. PVC insulated unsheathed single core copper in PVC cashing caping. | 80 | Mtr
4 | Supply, installation & tesing of 2 x 36 watt ceiling mounted optic luminaries with gright andodised aluminium relector & low glare PS paralite louver in modular/gypsum ceiling with 600 x 600 mm module square luminaries designed for 2 36 watt lamp. Havells/CH/Bajaj Make | 6 | Each
5 | Supplying with fitting and fixing MCCB incomer and MCB outgoing 8 way TPN (4+18 ) sheet steel phosphatised, power painted double door surface mounting vertical TPN MCB DB incorporated with bus bar, neutral link, earth bar and din rail etc.. complete with making necessary connection as specified and directed by deptt. (Havells/Legrand/Crabtree/Indoasian Make | 2 | Each
6 | Supplying, installation, testing and commissioning of decorative striplite luminaries with electronic ballast, end cap and 1 x 40 watt prewired fluorescent tube complete with all accessories including connection with 1.5 sw. mm. Single core copper wire as required and directed by deptt. (Bajaj /CG Havells /Phillips Make | 16 | Each
7 | Supplying with fitting and fixing 4+12 way sheet steel phosphatised, power painted double door surface mounting vertical MCB TPN MCB DB incorporated with bus bar, neutral link, earth bar and din rail etc. complete with making necessary connection as specified and directed by deptt. (Legrand/Havells/Crabtee/Indoasian Make | 2 | Each
8 | Supplying with fitting and fixing sheet steel phosphatised power painted single door surface mounting 4 way MCB enclosure and nrcessary connection as directed by deptt. . Legrand/Havells/Crabtree/Indiasian Make | 14 | Each
9 | Supplying with fitting and fixing sheet steel phosphatised power painted single door surface mounting 2 way MCB enclosure and nrcessary connection as directed by deptt. . Legrand/Havells/Crabtree/Indiasian Make | 4 | Each
10 | Supplying with fitting and fixing 10 kA 240/415 v 50 Hz. B-series MCB of following capacity complete with necessary connection and terminal lug as reqd.
| (a) 4 Pole 25 KA 125A MCCB (Legrand/Havells/Crabtree/Indoasian Make) | 2 | Each
| (c) 3 Pole 63A MCB (Legrand/Havells/Crabtree/IndiasianMake) | 12 | Each
| (e) 32 A single Pole MCB (Legrand/ Havells/Crabtree/Indoasian Make) | 24 | Each
| (f) 63 A 4 Pole MCB (Legrand/Havells/Crabtree/Indoasian Make) | 2 | Each
| (f) 40 A 4 Pole MCB (Legrand/Havells/Crabtree/Indoasian Make) | 14 | Each
| (g) 32 A double Pole MCB (Legrand/Havells/Crabtree/Indoasian Make) | 4 | Each
11 | Supply, installation & testing of GI Earth Station with 50mm. Dia and 3.00 mtr. Long heavy duty GI pipe with necessary 50mm dia GI fittings such as socket, tee, elbow, nipple and 65mm x 50mm size GI reducing socket for funnel incliuding locking arrangement 300mm x 300mm x 6mm hinged cover CI earth plate complete with digging of earth pit construction of brick chember and plastering the same in both side including refilling the pit with a layer of salt & charcoal and soil complete as specified and directed by department. | 2 | Each
12 | Supplying and laying of 8 SWG copper earth drawn through 15mm dia medium quality GI pipe from earth electrode (below GL) to electrical switchgears or electrical machineries including making necessary connection as approved , specified and directed by department. | 15 | Mtrs
13 | Supplying and laying of 3 x 10 sq.mm size PVC insulated and sheathed 11 kV grade solid aluminium armoured underground cable laid through existing cable trench/duct/cable tray/DDPE pipe including fitting required size of lugs at the both end of the calbe by using crimping tools and as specified and directed by department. (Havells/Finolex/Polycab Make) | 275 | Mtr
14 | Supplying including fitting & fixing of heavy duty 450 mm sweep 900 RPM single phase AC exhaust fan complete with all making hole etc as specified and directed by the department | 4 | Each
15 | Supplying including fitting & fixing of 400 mm sweep metal body metal blade SDX 120 AC wall fan on the wall complete with all necessary connection as required. | 3 | Each
16 | Making good by damage done including painting etc. | L/S
Total Tender Cost in Rs.
Rupees :
only